## Slide 1
Five .Yang
20200425
Error Trouble Shooting
LCAC ON/OFF type
2020

## Slide 2
Part 1
Necessary tools
1.Multimeter
2. Current clamp
3. Thermometer

## Slide 3
1.Multimeter
Function ：test resistance , current , voltage ,etc.
4. Switch to A to test current
Note：
Choose DC or AC according to demand
Choose the appropriate range
1.Rest to “OFF” before start testing
2. Switch to V before testing voltage.
Note：Choose DC or AC according to demand
3. Switch to Ω to test resistance.

## Slide 4
Function： Test running current
2. Current clamp
Note: Single-core wires go through the current clamp

## Slide 5
Function： Test air inlet & outlet temperature
3. Thermometer

## Slide 6
Part 2
Error code trouble
shooting guide

## Slide 7
E1 Indoor temperature sensor is abnormal
E2 Outdoor defrost sensor is abnormal
E3 Indoor coil sensor is abnormal
E7 Outdoor condensing mid temperature sensor is abnormal
Communication fault
Temp. sensor fault(5)
E8 Discharge temperature sensor is abnormal
IDU fault
Refrigerant circuit fault
Total 13 error codes

## Slide 8
Yes
Replace PCB
Whether the sensor connector is loose ?
Connect the connector again
Yes
Is sensor broken ?
Replace sensor
No
Broken
Connector is loose
1. Trouble shooting Guide
No

## Slide 9
2. Where are these sensors？
E1 Indoor temperature sensor is abnormal
E3 Indoor coil sensor is abnormal
E8 Discharge temperature sensor is abnormal
E2 Outdoor defrost sensor is abnormal
E7 Outdoor condensing mid temperature sensor is abnormal
20k
15k
50k
20k
20k

## Slide 10
3. Resistance comparison table
Sensor resistance at 25°C | Resistance comparison table
15KΩ | 
20KΩ | 
50KΩ | 

## Slide 11
F1 Communication abnormal between the outdoor unit and the Indoor unit
E5 Communication abnormal between the wired controller and indoor unit
Communication fault (2)
Temp. sensor fault
IDU fault
Refrigerant circuit fault
Total 13 error codes

## Slide 12
Check if the communication cable is broken.
Replace the communication cable
Rewiring according to the wiring diagram
Check if the communication cable to the indoor and outdoor terminal boards is wrong.
Replace ODU PCB
Replace IDU PCB
F1 Trouble shooting Guide
No
Yes
Yes
No
No
Yes
OVER

## Slide 13
F1 Communication abnormal between the outdoor unit and the Indoor unit
E5 Communication abnormal between the wired controller and indoor unit
Communication fault (2)
Temp. sensor fault
IDU fault
Refrigerant circuit fault
Total 13 error codes

## Slide 14
E5 Trouble shooting Guide
Check if the wired controller is abnormal
Replace wired controller
Replace the communication cable
Check if the communication cable is broken.
No
Yes
Yes
Replace IDU PCB
No

## Slide 15
E4 Fault with the drainage on Indoor unit
Communication fault
Temp. sensor fault
IDU fault (1)
Refrigerant circuit fault
Total 13 error codes

## Slide 16
E4 display logic
PUMP port
Float switch port
E4 error code display logic :
Float switch ports on PCB are normally closed circuit , once be disconnected then E4 will be displayed
water drainage pan
Float down connect
Float up disconnect
Full of water
Float switch working diagram

## Slide 17
E4 Trouble shooting Guide
E4 error
yes
Check water drainage pan
Whether full of water
Adjust the water drainage pipe or clean the water drainage pan
No
Check PCB
Remove float switch wiring, short connect Float switch port
Error
exists
Replace
PCB
Check float switch
Manual change the float to up and down (＞1 min)
Replace
Float switch
Up-error
Down – no error
Check the drain pump
Whether it can drain water normal
Error
exists
no error
abnormal
Replace the drain pump
E4 come again
after a while

## Slide 18
Communication fault
Temp. sensor fault
IDU fault
Refrigerant circuit fault(5)
Total 13 error codes
EA Discharge temperature too high
E9 Low pressure switch protection
E0 Lack of refrigerant
E6 Phase sequence abnormal
F9 High pressure Switch Protection

## Slide 19
F9/E9 display logic
F9/E9 error code display logic :
HP and LP switch ports on PCB are Normally closed circuit , once be disconnected then F9/E9 will be displayed
Each port contain two point

## Slide 20
F9/E9 Troubleshooting Guide
F9/E9 error
Error Still exists
Check HP/LP port and PCB
Remove wiring， short connect two
Point, then power reset ,
Replace PCB
No error
Check HP/LP switch
Reconnect switch wiring to PCB，power reset
Error
exists
No error
Replace
switch
Check installation of ODU
Whether poor heat exchange of ODU
Yes
Improve installation
No
Check the refrigerant system
Whether poor performance of indoor side
Whether abnormal current、 high pressure value
Vacuum pump, Check Air tightness, recharging refrigerant

## Slide 21
Communication fault
Temp. sensor fault
IDU fault
Refrigerant circuit fault(5)
Total 13 error codes
EA Discharge temperature too high
E9 Low pressure switch protection
E0 Lack of refrigerant
E6 Phase sequence abnormal
F9 High pressure Switch Protection

## Slide 22
E6 display logic
E6 Phase sequence abnormal logic :
Two current transformer detect the real time current of compressor wiring , once these
Two current value big different or no current , then F6 error be display
Two Current transformer
AC
contactor
Compressor red wiring
Compressor green wiring

## Slide 23
Check ODU power supply
Change the phase sequence of
Power supply
E6 Trouble shooting Guide
E6 error
Error Still
exists
Ok
No error
Check compressor wiring
Whether compressor wiring go through current transformer
no
yes
Reconnect
Check compressor wiring current value
current clamp test current
same
Replace current transformer
Big different
Check compressor & compressor terminal wire
Make sure correct wiring

## Slide 24
Communication fault
Temp. sensor fault
IDU fault
Refrigerant circuit fault(5)
Total 13 error codes
EA Discharge temperature too high
E9 Low pressure switch protection
E0 Lack of refrigerant
E6 Phase sequence abnormal
F9 High pressure Switch Protection

## Slide 25
E0 display logic
E0 Lack of refrigerant logic :
After compressor working more than 6min, if detect TR-TE d＜2℃， then E0 error will be display
Indoor Units
TR
TE

## Slide 26
E0 Trouble shooting Guide
Check TR sensor
Repower and operation cooling
Mode , detect air return and air outlet temperature difference
E0 error
＜2℃
Replace
TR sensor
＞2℃
Check TE sensor
Touch the Evaporator ,whether low temperature
yes
NO
Replace
TE sensor
Check installation of ODU
Whether poor heat exchange of ODU
no
Improve installation
Vacuum pump, Check Air tightness, recharging refrigerant

## Slide 27
Communication fault
Temp. sensor fault
IDU fault
Refrigerant circuit fault(5)
Total 13 error codes
EA(F2) Discharge temperature too high
E9 Low pressure switch protection
E0 Lack of refrigerant
E6 Phase sequence abnormal
F9 High pressure Switch Protection

## Slide 28
EA(F2) display logic
EA(F2) Discharge temperature too high logic :
Compressor discharge temperature sensor detected Td ≥120℃ and Lasts for 10s, whole system will stop running, then EA（F2） error be display
Exhaust(Discharge)
Temperature sensor

## Slide 29
EA（F2） Trouble shooting Guide
Check temperature sensor
check exhaust temperature of
The exhaust piping
EA(F2) error
High
Replace
sensor
Low
temperature
Check fan motor
Whether IDU and ODU fan can run normally
no
yes
Replace
Fan motor
Check installation of ODU
Whether poor heat exchange of ODU
no
Yes
Improve installation
Check the refrigerant system
Whether poor performance of indoor
Vacuum pump, Check Air tightness, recharging refrigerant
Abnormal noise of compressor
Error again
Replace compressor